## Sheet1
1095040 - NDSU Engineering Building 2024
Tag | Model | Supply Fan |  |  |  | Supply Fan Motor |  |  | Unit Electrical |  |  |  | Cooling Coil | [11 empty] | Heating Coil
|  | Airflow (CFM) | Drive Type | E.S.P. | Primary Filter | Power | Electrical | Quantity | FLA | MCA | MROPD | SCCR | Airflow (CFM) | Capacity |  | Entering Air |  | Leaving Air |  | Fluid |  |  |  |  | Airflow (CFM) | Capacity | Entering Air | Leaving Air | Fluid
|  |  | Drive Type | [10 empty] | Sensible | Total | DB | WB | DB | WB | Type | Flow Rate | Pressure Drop | EWT | LWT |  | Sensible | DB | DB | Type | Flow Rate | Pressure Drop | EWT | LWT
|  |  |  | (inH₂O) |  | (HP) | (Voltage) |  | (A) | (A) | (A) |  |  | (Btu/hr) | (Btu/hr) | (°F) | (°F) | (°F) | (°F) |  | (gpm) | (ft H₂O) | (°F) | (°F) |  | (Btu/hr) | (°F) | (°F) |  | (gpm) | (ft H₂O) | (°F) | (°F)
AHU-0 | BCVE0501 | 4000 | Direct | 0.25 | 2 inch MERV 8 | 2 x 4.42 Hp | 460/60/3 | 2 | 5.6 | 12.6 | 15 | 5 kA | 4000 | 97010 | 109137 | 77.0 | 63.9 | 54.8 | 54.8 | Ethylene | 16.6 | 2.62 | 42.0 | 57.0
AHU-10 | BCVE0301 | 1650 | Direct | 0.75 | 2 inch MERV 8 | 4.42 Hp | 460/60/3 | 1 | 5.6 | 7.0 | 15 | 5 kA | 1650 | 40888 | 47575 | 77.0 | 63.9 | 54.3 | 54.2 | Ethylene | 7.2 | 4.34 | 42.0 | 57.0 | 1650 | 69768 | 57.0 | 95.7 | Ethylene | 8.0 | 1.04 | 160.0 | 140.8
AHU-11 | BCVE0501 | 4000 | Direct | 0.25 | 2 inch MERV 8 | 2 x 4.42 Hp | 460/60/3 | 2 | 5.6 | 12.6 | 15 | 5 kA | 4000 | 97045 | 109219 | 77.0 | 63.9 | 54.8 | 54.8 | Ethylene | 16.6 | 2.63 | 42.0 | 57.0