## Sheet1
1095040 - NDSU Engineering Building 2024
Unit | [6 empty] | Supply Fan | [11 empty] | Chilled Water Coil | [13 empty] | Combination Coil | [27 empty] | Hot Water Coil | [10 empty] | Panel Filter | [7 empty] | Mixing Box | [7 empty] | Combination Filter
Tag | Qty | Model | Length (in) | Weight (lb) | External Dimensions* |  | Fan | [7 empty] | Motor |  |  |  | Sensible Capacity (Btu/hr) | Total Capacity (Btu/hr) | EAT-DB °F | EAT-WB °F | LAT-DB °F | LAT-WB °F | F.V. (ft/min) | A.P.D. (inH2O) | EWT °F | LWT °F | Flow Rate (GPM) | W.P.D. (ftH2O) | Rows | FPI | A.P.D. (inH2O) | Cooling | [14 empty] | Heating | [11 empty] | Total Capacity (Btu/hr) | EAT-DB °F | LAT-DB °F | F.V. (ft/min) | A.P.D. (inH2O) | EWT °F | LWT °F | Flow Rate (GPM) | W.P.D. (ftH2O) | Rows | FPI | Filter | Type | Filter Qty - Sizes | Depth | Efficiency | Clean PD (inH2O) | Dirty PD (inH2O) | Mean PD (inH2O) | Filter | Type | Filter Qty - Sizes | Depth | Efficiency | Clean PD (inH2O) | Dirty PD (inH2O) | Mean PD (inH2O) | Panel Filter | [6 empty] | Bag Filter
[5 empty] | Supply |  | Type | Qty | Class | Airflow (CFM) | RPM | BHP | E.S.P. (inH2O) | T.S.P. (inH2O) | Voltage | Power (HP) | RPM | Control | [15 empty] | Sensible Capacity (Btu/hr) | Type | Total Capacity (Btu/hr) | EAT-DB °F | EAT-WB °F | LAT-DB °F | LAT-WB °F | F.V. (ft/min) | Suct. Temp. °F | EWT °F | LWT °F | Flow Rate (GPM) | W.P.D. (ftH2O) | Rows | FPI | Total Capacity (Btu/hr) | Type | EAT-DB °F | LAT-DB °F | F.V. (ft/min) | EWT °F | LWT °F | Flow Rate (GPM) | W.P.D. (ftH2O) | Steam PD (psi) | Rows | FPI | [27 empty] | Type | Filter Qty - Sizes | Depth | Efficiency | Clean PD (inH2O) | Dirty PD (inH2O) | Mean PD (inH2O) | Type | Filter Qty - Sizes | Depth | Efficiency | Clean PD (inH2O) | Dirty PD (inH2O) | Mean PD (inH2O)
[5 empty] | Height (in) | Width (in)
AHU-7 2-7-25 | 1 | CAH023GDCM | 122 | 3495.29 | 54 | 84 | EBM450-RPII | 2 | N/A | 5000 | 2313 | 4.34 | 1.5 | 3.56 | 460/60/3 | 5.97 | 2480 | Integrated Drive | [14 empty] | 1.21 | 392684 | Standard | 498040 | 86.8 | 67.3 | 50.9 | 50.6 | 483 | 0 | 42 | 57.2 | 74.8 | 17.7 | 8 | 11 | 938477 | 3 to 12 rows | 5 | 90.8 | 483 | 160 | 119.6 | 51.3 | 16.1 | 0 | 3 | 9 | [19 empty] | Flat panel | Pre Pleat (MERV 13) | 8 - 24.00 x 20.00 | 2 | MERV 13 | 0.26 | 1 | 0.63
AHU-8 | 1 | CAH018GDCM | 120 | 2907.69 | 48 | 78 | EBM450-RPII | 2 | N/A | 4065 | 2116 | 3.35 | 1.5 | 3.49 | 460/60/3 | 5.97 | 2480 | Integrated Drive | [14 empty] | 1.12 | 240922 | Standard | 331007 | 78.3 | 64.9 | 51.2 | 51 | 462 | 0 | 42 | 57.2 | 49.6 | 18.6 | 8 | 10 | 388417 | 1 & 2 rows | 49 | 92.7 | 484 | 160 | 118.3 | 20.6 | 3.6 | 0 | 2 | 9 | [19 empty] | Flat panel | Pre Pleat (MERV 13) | 6 - 20.00 x 24.00 | 2 | MERV 13 | 0.29 | 1 | 0.64
AHU-9 | 1 | CAH030GDCM | 130 | 4354.24 | 54 | 108 | EBM630-RPII | 2 | N/A | 6765 | 1590 | 6.25 | 1.5 | 3.47 | 460/60/3 | 7.01 | 1650 | Integrated Drive | [14 empty] | 1.17 | 394786 | Standard | 537065 | 78.3 | 64.9 | 51.6 | 51.4 | 488 | 0 | 42 | 57.1 | 81.3 | 11.8 | 10 | 8 | 623357 | 1 & 2 rows | 49 | 91.1 | 504 | 160 | 118.9 | 33.5 | 9 | 0 | 2 | 10 | [19 empty] | Flat panel | Pre Pleat (MERV 13) | 2 - 24.00 x 12.00 2 - 24.00 x 20.00 6 - 24.00 x 24.00 | 4 | MERV 13 | 0.17 | 1 | 0.59
AHU-E1 | 1 | CAH016GDCM | 148 | 2777.92 | 48 | 72 | DEL355 | 2 | N/A | 3885 | 3222 | 3.08 | 1.5 | 3.23 | 200/60/3 | 4.42 | 3230 | Integrated Drive | [14 empty] | 1.05 | 217388 | Standard | 312490 | 80 | 67 | 54.4 | 53.9 | 486 | 0 | 42 | 57.1 | 46.1 | 11.2 | 6 | 11 | 435461 | 1 & 2 rows | 40 | 91.3 | 512 | 160 | 119 | 23.1 | 4 | 0 | 2 | 10 | [19 empty] | Angled panel | Pre Pleat (MERV 13) | 3 - 24.00 x 20.00 6 - 24.00 x 24.00 | 4 | MERV 13 | 0.08 | 1 | 0.54
AHU-E2 | 1 | CAH013GDCM | 136 | 2356.02 | 48 | 60 | EBM355-RPII | 2 | N/A | 2565 | 2681 | 1.97 | 1.5 | 2.92 | 200/60/3 | 3.45 | 3230 | Integrated Drive | [14 empty] | 0.72 | 143322 | Standard | 206275 | 80 | 67 | 54.5 | 53.9 | 403 | 0 | 42 | 57.1 | 30.4 | 11.6 | 5 | 12 | 291982 | 1 & 2 rows | 40 | 92.1 | 430 | 160 | 118.4 | 15.3 | 1.6 | 0 | 2 | 10 | [19 empty] | Angled panel | Pre Pleat (MERV 13) | 3 - 24.00 x 12.00 3 - 24.00 x 20.00 3 - 24.00 x 24.00 | 4 | MERV 13 | 0.06 | 1 | 0.53
AHU-E3 | 1 | CAH037GDCM | 166 | 4598.89 | 72 | 96 | EBM355-RPII | 6 | N/A | 2482 | 2656 | 1.92 | 1.5 | 2.98 | 200/60/3 | 3.45 | 3230 | Integrated Drive | [14 empty] | 0.77 | 418860 | Standard | 607093 | 80 | 67 | 54.3 | 53.7 | 431 | 0 | 42 | 57.3 | 88.3 | 17.6 | 5 | 12 | 849506 | 1 & 2 rows | 40 | 92.2 | 447 | 160 | 118.3 | 44.3 | 7 | 0 | 2 | 9 | [19 empty] | Angled panel | Pre Pleat (MERV 13) | 4 - 24.00 x 20.00 12 - 24.00 x 24.00 | 4 | MERV 13 | 0.09 | 1 | 0.54
AHU-M3 3-20-2025 | 1 | CAH015GDCM | 160 | 2906.65 | 48 | 66 | EBM630-RPII | 1 | N/A | 6000 | 1568 | 5.95 | 1.5 | 3.77 | 460/60/3 | 7.08 | 1750 | Integrated Drive | [14 empty] | 1.01 | 170143 | Standard | 242832 | 80 | 67 | 54.1 | 53.8 | 418 | 0 | 42 | 57.2 | 36.5 | 7.2 | 6 | 10 | 344268 | 1 & 2 rows | 40 | 92.5 | 443 | 180 | 138 | 18.7 | 2.3 | 0 | 2 | 9 | [19 empty] | None | NA |  | NA | NA | 0 | 0 | 0 | Pleated (MERV 8) | 6 - 20.00 x 20.00 | 2 | MERV 8 | 0.16 | 1 | 0.58 | Pre Pleat (MERV 13) | 6 - 20.00 x 20.00 | 4 | MERV 13 | 0.16 | 1 | 0.58
MAU-12 | 1 | CAH028GDCM | 172 | 4022.01 | 60 | 90 | EBM450-RPII | 2 | N/A | 5000 | 1993 | 2.68 | 0.75 | 1.93 | 460/60/3 | 3.51 | 2140 | Integrated Drive | 280351 | 391796 | 95 | 75 | 69.4 | 64.5 | 390 | 0.24 | 42 | 59.1 | 50.8 | 7.3 | 4 | 6 | [28 empty] | 1174555 | -30 | 77.4 | 405 | 0.23 | 160 | 119.1 | 62.4 | 17.1 | 2 | 11 | Flat panel | Pleated (MERV 8) | 3 - 12.00 x 24.00 4 - 20.00 x 20.00 4 - 20.00 x 24.00 | 2 | MERV 8 | 0.14 | 1 | 0.57 | None | NA |  | NA | NA | 0 | 0 | 0
*Note, external dimension values do not include base rails, coil connectors, drain connectors and/or control boxes.